## February FireLight Ground Mount
MONTHLY REPORT SUMMARY FEBRUARY 2017
| Project | Month-Year | Insolation |  | Energy Production |  |  | Performance
|  |  | Actual | Reference | Measured | Expected | Budget | Actual | Actual | Weather
|  |  | [kWh/m2] | [kWh/m2] | [kWh] | [kWh] | [kWh] | Budget | Expected | Performance %
1 | 1935 Drew | 2017-02-01 | 105.59 | 90 | 75000 | 104420.2974 | 89003 | 84.27% | 71.83% | 117.3%
2 | 51 Fitzgerald | 2017-02-01 | 94.53 | 85 | 83000 | 99004.0493 | 89023 | 93.23% | 83.83% | 111.2%
3
4
5
6
7
8
9
10
11
12
13
14
15
| TOTAL |  | 200.12 | 175 | 158000 | 203424.3467 | 178026 | 88.75% | 77.67% | 114.3%
Notes: 2) Hwy 2 S: a. Oct. 2: inverter 6C went offline due to fault. Site tech replaced and torqued the loosefan wiring 3) Norfolk: a. Oct. 6: Main AC breaker opened caused by the auto reclosure of the Norfolk TS. 4) Rutley: a. On going: Pile remediation work in progress. Trackers were sequentially stalled to give access to workers. 5) Alfred: a. Oct. 24-28: Inverters were underperforming because the EPC contractors on site were mapping and labeling the devices. 6) Actual Production and Insolation measurements were taken from SCADA.