## Sheet1
GCS Performance Index Conceptual Calculation
Legends
Inputs
Output
Site Specific Inputs: |  | Comment
DC Nameplate Capacity (kW): | 13305 | This is constant. Will never change. But it would be good to make it editable as well just in case we add more solar panels in the future.
AC Nameplate Capacity (kW) | 10000 | This is constant. Will never change. But it would be good to make it editable as well just in case we add more Inverter in the future.
Module Power Coefficient (%/Co) | -0.43 | Editable; Constant/Default Value
Inverter Efficiency (CEC) %: | 98% | Editable; Constant/Default Value
Transformer Loss if Present (%) | 1.5% | Editable; Constant/Default Value
Other Loss Assumptions (%): | 2% | Editable; Constant/Default Value
Data Inputs:
Avg Irradiance POA (W/m2) | 594.816 | This is the IRR_POA, or IRR_CMP_POA value; average in 60Minutes
Time-step (minutes) | 60 | 60 Minute data
Average Module Temp (Degrees C) | 37 | Back of Module Temperature (PANELT value)
Measured Energy (kW) | 7482.58 | Total Inverter Output (kW); Average in 60 Minutes ( If there are multiple inverters, We can just sum the total of the multiple inverters to make it simpler.)
Formula (Plain English) | Theoretical Output = (Sunshine IRR/1000) X DC Nameplate Capacity - Module Temperature Losses - inverter efficiency losses (limited to inverter nameplate)- transformer losses - other system losses
Theoretical Output Calculations:
Maximum Theoretical Output kW | 7914.0269 | ('Avg Irradiance POA' / 1000) * 'DC Name Plate Capacity'
Temperature Losses kW | 40.8364 | ('Maximum Theoretical Output kW'*('Module Power Co-efficient' * (25 - 'Avg Module Temp'))) / 1000
Inverter Losses (kW) | 157.4638 | (1-'Inverter Efficiency) * ('Maximum Theoritcal Output' - 'Temp Losses kW')
Inverter Clipping (Over Nameplate) Loss (kW) | 0 | if ('Maximum Theory Output kW' - 'Temperature Losses kW' - 'Inverter Losses kW') > 'AC Name plate Capacity') then 'Maximum Theory Output kW' - 'Temperature Losses kW' - 'Inverter Losses kW' -'AC Name plate Capacity' , else 0
Transformer Losses (kW) | 115.7359 | ('Maximum Theory Output kW' - 'Temperature Losses kW' - 'Inverter Losses kW' - 'Inverter Clipping Loss kW') * (Transformer Loss %)
Other System Losses (kW) | 151.9998 | ('Maximum Theory Output kW' - 'Temperature Losses kW' - 'Inverter Losses kW' - 'Inverter Clipping Loss kW' - 'Transformer Loss kW') * 'Other Loss Assumption'
Total Losses (%) | 5.889% | ( 'Temperature Losses kW' + 'Inverter Losses kW' + 'Inverter Clipping Loss kW' + 'Transformer Loss kW' + 'Other System Losses') / 'Maximum Theoretical Output'
Theoretical Output (kW) | 7447.991 | ('Maximum Theory Output kW' - 'Temperature Losses kW' - 'Inverter Losses kW' - 'Inverter Clipping Loss kW' - 'Transformer Loss kW' - 'Other System Losses')
GCS Performance Index: | 100.5% | ' Measured Energy kW' / 'Theoretical Output kW'. This is the Performance Ratio (PR) or Performance Index (PI) we would like to display on the dashboard.
Note on C26: Jerick: The 25 here is contstant. As per the module specs, if the temperature goes lower or higher than 25C, the efficiency also is impacted.