## Hwy 2 and Odessa (hidden)
OCTOBER FIRELIGHT GROUNDMOUNT REPORT
Project | Month-Year | Insolation |  | Energy Production |  |  | Performance |  |  | Comments: | Weather | Availability | Performance | Performance
|  | Actual | Reference | Actual | Expected | Reference | OPR | IPR | WPR |  | % | % | % | OPR | IPR | WPR
|  | [kWh/m2] | [kWh/m2] | [kWh] | [kWh] | [kWh] | [%] | [%] | [%] |  | #REF! | #REF! | #REF! | [%] | [%] | [%]
SunE Hwy 2 S | 2014-10-15 | 93.5 | #REF! | 1023164 | #REF! | 1165304.25 | [7 empty] | #REF! | 87.8% | #REF!
|  |  |  | 12839562.1778 | 13443302.3844 | 13918493.25 | [7 empty] | 95.51% | 92.25% | 96.59%
YTD |  |  |  | 13862726.1778 | #REF! | 15083797.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 91.9% | #REF!
SunE Odessa | 2014-10-16 | 87 | #REF! | 988179 | #REF! | 1150480 | [7 empty] | #REF! | 85.89% | #REF!
|  |  |  | 12797945.7416 | 13022451.0867 | 13522080 | [7 empty] | 98.28% | 94.64% | 96.31%
YTD |  |  |  | 13786124.7416 | #REF! | 14672560 | [7 empty] | #REF! | 93.96% | #REF!
Notes: 1) Actual Production were taken from HONI Meter and the Insolation measurements were taken from SCADA.

## February FireLight Ground Mount
MONTHLY REPORT SUMMARY FEBRUARY 2017
| Project | Month-Year | Insolation |  | Energy Production |  |  | Performance
|  |  | Actual | Reference | Measured | Expected | Budget | Actual | Actual | Weather
|  |  | [kWh/m2] | [kWh/m2] | [kWh] | [kWh] | [kWh] | Budget | Expected | Performance %
1 | 1935 Drew | 2017-02-01 | 105.59 | 90 | 75000 | 104420.2974 | 89003 | 84.27% | 71.83% | 117.3%
2 | 51 Fitzgerald | 2017-02-01 | 94.53 | 85 | 83000 | 99004.0493 | 89023 | 93.23% | 83.83% | 111.2%
3
4
5
6
7
8
9
10
11
| TOTAL |  | 200.12 | 175 | 158000 | 203424.3467 | 178026 | 88.75% | 77.67% | 114.3%
Notes: 2) Hwy 2 S: a. Oct. 2: inverter 6C went offline due to fault. Site tech replaced and torqued the loosefan wiring 3) Norfolk: a. Oct. 6: Main AC breaker opened caused by the auto reclosure of the Norfolk TS. 4) Rutley: a. On going: Pile remediation work in progress. Trackers were sequentially stalled to give access to workers. 5) Alfred: a. Oct. 24-28: Inverters were underperforming because the EPC contractors on site were mapping and labeling the devices. 6) Actual Production and Insolation measurements were taken from SCADA.
1) Measured Energy (kWh) were taken from the SCADA. The Measured Energy (kWh) and Weather Performance are only preliminary and not audited.
Note on G5: astejada: ("MEASURED INSOLATION"/INSOLATION REFERENCE") * (REFERENCE PRODUCTION KWH)
Note on I5: astejada: "MEASURED PRODUCTION" / "REFERENCE PRODUCTION"
Note on J5: astejada: "MEASURED PRODUCTION" / "EXPECTED PRODUCTION"
Note on K5: astejada: "EXPECTED KWH" / "REFERENCE KWH"

## Sept FireLight Q3 (hidden)
FIRELIGHT GROUNDMOUNT REPORT (Q3 Report)
| Project | Month-Year | Insolation |  | Energy Production |  |  | Performance |  |  | Comments: | Weather | Availability | Performance | Performance
|  |  | Actual | Reference | Actual | Expected | Reference | OPR | IPR | WPR |  | % | % | % | OPR | IPR | WPR
|  |  | [kWh/m2] | [kWh/m2] | [kWh] | [kWh] | [kWh] | [%] | [%] | [%] |  | #REF! | #REF! | #REF! | [%] | [%] | [%]
| SunE Sandhurst | 2014-07-14 | 231 | 156.5 | #REF! | 3168438.9659 | 2146583.109 | [7 empty] | #REF! | #REF! | 147.6%
|  | 2014-08-14 | 205 | 209.1 | #REF! | 1715871.8901 | 1750189.328 | [7 empty] | #REF! | #REF! | 98.04%
|  | 2014-09-14 | 179 | 156.5 | #REF! | 1541937.0978 | 1348118.1889 | [7 empty] | #REF! | #REF! | 114.4%
| Q3 - 2014 |  | 615 | 522.1 | #REF! | 6426247.9539 | 5244890.6258 | [7 empty] | #REF! | #REF! | 117.8%
| SunE Rutley Gen | 2014-07-14 | 218.36 | 245.5 | #REF! | 1904635.2975 | 2141362.7291 | [7 empty] | #REF! | #REF! | 88.95%
|  | 2014-08-14 | 200 | 205.4 | #REF! | 2085066.9222 | 2141363.7291 | [7 empty] | #REF! | #REF! | 97.37%
|  | 2014-09-14 | 153.7112 | 158.5 | #REF! | 1421422.8226 | 1465706.9432 | [7 empty] | #REF! | #REF! | 96.98%
| Q3 - 2014 |  | 572.0712 | 609.4 | #REF! | 5411125.0423 | 5748433.4014 | [7 empty] | #REF! | #REF! | 93.87%
| SunE Hwy 2 S | 2014-07-14 | 180.7 | 194.3 | #REF! | 1836736.2171 | 1974974.25 | [7 empty] | #REF! | #REF! | 93%
|  | 2014-08-14 | 166.5 | 171.8 | #REF! | 1688757.9897 | 1742514.25 | [7 empty] | #REF! | #REF! | 96.92%
|  | 2014-09-14 | 157 | 145.5 | #REF! | 1615588.5378 | 1497249.25 | [7 empty] | #REF! | #REF! | 107.9%
| Q3 - 2014 |  | 504.2 | 511.6 | #REF! | 5141082.7445 | 5214737.75 | [7 empty] | #REF! | #REF! | 98.55%
| SunE Odessa | 2014-07-14 | 175 | 197.8 | #REF! | 1736821.9161 | 1963105 | [7 empty] | #REF! | #REF! | 88.47%
|  | 2014-08-14 | 165.52 | 172.6 | #REF! | 1637928.7648 | 1707990 | [7 empty] | #REF! | #REF! | 95.9%
|  | 2014-09-14 | 150 | 144 | #REF! | 1506229.1667 | 1445980 | [7 empty] | #REF! | #REF! | 104.2%
| Q3 - 2014 |  | 490.52 | 514.4 | #REF! | 4880979.8475 | 5117075 | [7 empty] | #REF! | #REF! | 95.36%
| SunE Alfred | 2014-07-14 | 157 | 183.5 | #REF! | 1692246.1035 | 1977880 | [7 empty] | #REF! | #REF! | 85.56%
|  | 2014-08-14 | 188.29 | 174.1 | #REF! | 2041080.9041 | 1887260 | [7 empty] | #REF! | #REF! | 108.2%
|  | 2014-09-14 | 148.47 | 140.7 | #REF! | 1645363.1119 | 1559255 | [7 empty] | #REF! | #REF! | 105.5%
| Q3 - 2014 |  | 493.76 | 498.3 | #REF! | 5378690.1196 | 5424395 | [7 empty] | #REF! | #REF! | 99.09%
``
| SunE Unity | 2014-07-14 | 175.28 | 190.1 | #REF! | 1861831.3519 | 2019250 | #REF! | [6 empty] | #REF! | #REF! | 92.2%
|  | 2014-08-14 | 168.09 | 177 | #REF! | 1790386.4186 | 1885290 | [7 empty] | #REF! | #REF! | 94.97%
|  | 2014-09-14 | 153.44 | 150.1 | #REF! | 1670477.0526 | 1634115 | [7 empty] | #REF! | #REF! | 102.2%
| Q3 - 2014 |  | 496.81 | 517.2 | #REF! | 5322694.8232 | 5538655 | [7 empty] | #REF! | #REF! | 96.06%
| SunE Norfolk | 2014-07-14 | 184.55 | 189.4 | #REF! | 1765445.5339 | 1811841.6912 | [7 empty] | #REF! | #REF! | 97.44%
|  | 2014-08-14 | 174.64 | 171.3 | #REF! | 1678336.266 | 1646237.9888 | [7 empty] | #REF! | #REF! | 101.9%
|  | 2014-09-14 | 152.92 | 138.7 | #REF! | 1517915.1307 | 1376764.5085 | [7 empty] | #REF! | #REF! | 110.3%
| Q3 - 2014 |  | 512.11 | 499.4 | #REF! | 4961696.9305 | 4834844.1884 | [7 empty] | #REF! | #REF! | 102.5%
| SunE Erie Ridge | 2014-07-14 | 235.37 | 238 | 1804066 | 1762149.4936 | 1781839.5695 | [7 empty] | 102.4% | 101.2% | 98.89%
|  | 2014-08-14 | 211.7 | 204 | 1679227 | 1595872.7896 | 1537827.3457 | [7 empty] | 105.2% | 109.2% | 103.8%
|  | 2014-09-14 | 171.7 | 161 | 1320973 | 1330932.1946 | 1247991.1668 | [7 empty] | 99.25% | 105.8% | 106.6%
| Q3 - 2014 |  | 618.77 | 603 | 4804266 | 4688954.4778 | 4567658.0819 | [7 empty] | 102.5% | 105.2% | 102.6%

## Erie Ridge Q2 (hidden)
FIRELIGHT GROUNDMOUNT REPORT (Q2 Report)
Project | Month-Year | Insolation |  | Energy Production |  |  | Performance |  |  | Comments: | Weather | Availability | Performance | Performance
|  | Actual | Reference | Actual | Expected | Reference | OPR | IPR | WPR |  | % | % | % | OPR | IPR | WPR
|  | [kWh/m2] | [kWh/m2] | [kWh] | [kWh] | [kWh] | [%] | [%] | [%] |  | #REF! | #REF! | #REF! | [%] | [%] | [%]
SunE Erie Ridge | 2014-04-01 | 173.08 | 173 | 1434204 | 1397662.229 | 1397016.2099 | [7 empty] | 102.6% | 102.7% | 100%
| 2014-05-01 | 206.83 | 237 | 1665599 | 1600521.0212 | 1833986.7622 | [7 empty] | 104.1% | 90.82% | 87.27%
| 2014-06-01 | 245.03 | 230 | 1887631 | 1863134.4058 | 1748850.8074 | [7 empty] | 101.3% | 107.9% | 106.5%
Q2 - 2014 |  | 624.94 | 640 | 4987434 | 4861317.656 | 4979853.7795 | [7 empty] | 102.6% | 100.2% | 97.65%

## Firelight Ground Mount (hidden)
[15 empty] | Target | 99%
| Weather |  | Project | Month | Weather Performance | PRODUCTION |  |  |  |  | AVAILABILITY (energy-weighted) |  |  |  | RECONCILIATION TO BUDGET
[6 empty] | Budget | Expected | Actual | Actual Budget | Actual Expected | Grid Energy Loss | Plant Energy Loss | Plant Availability | Gross Availability | Weather | Availability | Performance
Measured | Modelled | WPR |  |  | % | kWh | kWh | kWh | % | % | kWh | kWh | % | % | % | % | %
185.5606 | #REF! | #REF! | SunE Sandhurst | 2014-09-01 | #REF! | 1348118 | #REF! | 1685697 | 125% | #REF! | 90052.4194 | 0 | 100% | 94.93% | #REF! | -4.071% | #REF!
153.7112 | #REF! | #REF! | SunE Rutley Gen | 2014-09-01 | #REF! | 1465707 | #REF! | 1473449 | 100.5% | #REF!
156.3082 | #REF! | #REF! | SunE Hwy 2 S | 2014-09-01 | #REF! | 1497249 | #REF! | 1478608 | 98.75% | #REF!
143.493 | #REF! | #REF! | SunE Odessa | 2014-09-01 | #REF! | 1445980 | #REF! | 1468602 | 101.6% | #REF!
148.47 | #REF! | #REF! | SunE Alfred | 2014-09-01 | #REF! | 1559255 | #REF! | 1495637 | 95.92% | #REF!
153.51 | #REF! | #REF! | SunE Unity | 2014-09-01 | #REF! | 1634115 | #REF! | 1490946 | 91.24% | #REF!
152.92 | #REF! | #REF! | SunE Norfolk | 2014-09-01 | #REF! | 1376765 | #REF! | 1580789 | 114.8% | #REF!
169.3 | #REF! | #REF! | SunE Erie Ridge | 2014-09-01 | #REF! | 1247991 | #REF! | 1320973 | 105.8% | #REF!
Note: The Actual kWh were taken from Sun Edison's SCADA. The Weather Performance (%) is only preliminary and not audited.
#REF!
at CSI estimate of 565,000, Performance is 25.5%
March Target | 134
Prorated | 112.3871

## Ground_Mounts (hidden)
Project | Actual Total Energy Usage (kWh) | September IE Expectation (kWh) | Actual Expected | IPR
SunE Sandhurst | 1685697 | #REF! | #REF! | 121.9%
SunE Rutley Gen | 1473449 | #REF! | #REF! | 102.7%
SunE Hwy 2 S | 1478608 | #REF! | #REF! | 98.68%
SunE Odessa | 1468602 | #REF! | #REF! | 105.2%
SunE Alfred | 1495637 | #REF! | #REF! | 95.96%
SunE Unity | 1490946 | #REF! | #REF! | 88.75%
SunE Norfolk | 1580789 | #REF! | #REF! | 113.3%
SunE Erie Ridge | 1320973 | #REF! | #REF! | 100.8%