## DailyProductionReport
Daily Solar Energy Production Report
Date: | February-22-2017
Production Details for Operational Sites
[5 empty] | Monthly Budget Production |  | Month-to-Date |  | Daily Budget Production |  |  | Daily Measured Production |  |  | Month-to-date Performance
No. | Project Name | Commercial Operational Date | Capacity |  | Monthly Budget | IE POA Insolation | Total Insolation | Total Energy | Daily Production | Daily Expected | Daily Insolation | Measured POA Insolation | Measured Inverter Production | Gen Meter Reading | Actual/Budget | Actual/Expected | Weather Performance
|  |  | (kW AC) | (kW DC) | kWh | kWh/m2 | kWh/m2 | kWh | kWh | kWh | kWh/m2 | kWh/m2 | kWh | kWh | % | %
1 | 125 Bermondsey | 21/02/2017 | 450 | 653 | 36628.72 | 80.5 | 50.58 | 16999.45 | 1308.1686 | 541.468 | 2.875 | 1.19 | 673.13 |  | 59.07% | 73.86% | 79.97%
2 | 1935 Drew | 21/02/2017 | 150 | 162.7 | 8969.66 | 69.9 | 50.24 | 4688.98 | 320.345 | 142.4367 | 2.4964 | 1.11 | 163.84 |  | 66.53% | 72.73% | 91.48%
3 | 1755 Brimley | 21/02/2017 | 500 | 602.91 | 24670.57 | 81.7 | 51.46 | 7465.39 | 881.0918 | 344.2405 | 2.9179 | 1.14 | 157.22 |  | 38.51% | 48.04% | 80.16%
4 | 200 Bullock | 21/02/2017 | 250 | 306.24 | 17778.57 | 82.3 | 51.56 | 7685.77 | 634.9489 | 261.386 | 2.9393 | 1.21 | 353.05 |  | 55.02% | 69% | 79.73%
5 | 51 Gerry Fitzgerald | 21/02/2017 | 500 | 611.3 | 34738.46 | 82.8 | 47.92 | 23449.43 | 1240.6593 | 465.6967 | 2.9571 | 1.11 | 639.86 |  | 85.91% | 116.6% | 73.66%
| TOTAL: |  | 1850 | 2336.15 | 122785.98 | 397.2 | 251.76 | 60289.02 | 4385.2136 | 1755.228 | 14.1857 | 5.76 | 1987.1 |  | 62.49% | 77.47% | 80.67%
Days in a Month | 28 | We do not to show this! I just used this for Calculations.
Total Days | 22 | We do not to show this! I just used this for Calculations.
Note on J10: Jerick: "Budget Production Monthly Budget, kWh" / "# of days in a month"
Note on K10: Jerick: "Daily Production kWh" * ( "Measured POA Insolation, kWh/m2" / "Daily Budget Energy Production Daily Insolation kWh/m2" )
Note on L10: Jerick: "IE POA Insolation kWh/m2" / "# of days in a month"
Note on O10: Jerick: Summary of the kWh_rec (kWh) from the Gen Meter. Please take the data from 12:00AM to 11:59PM for 1 day data. See Attached Sample.
Note on P10: Jerick: "Total Energy, kWh" / ("Daily Budget Production, kWh" * "Total Number of Days")
Note on Q10: Jerick: "Month to date Total Energy, kWh" / (("Daily Production, kWh" * "Total Number of Days") * "Weather Performance %" )
Note on R10: Jerick: "Month toDate Total Insolation, kWh/m2" / ("Daily Insolation, kWh/m2" * "Total of Days")